## RightSizeMeterForm
Town of Burlington
Water Customer Data Sheet
[12 empty] | Under 1300 | Equal of Over 1300
Customer: |  |  | Type of Occupancy: |  |  |  |  | Select Type of Occupany from Dropdown box |  | 0 | Residential | 16.01 | 50.003
|  |  | (commercial or residential) | [6 empty] | 0 | Commercial | 38.6 | 130.003
Building Address: |  | By: | [8 empty] | GPM | 0 | 0
Phone:
[11 empty] | GPM to use | 0
| Fixture | Value @ 60 PSI |  | Number of Fixtures |  | Total Value
| Bathtub | 8 | x |  | = | 0 | [5 empty] | Occupancy Drop Down
| Bedpan Washers | 10 | x |  | = | 0 | [5 empty] | Residential
| Bidet | 2 | x |  | = | 0 | [5 empty] | Commercial
| Dental Unit | 2 | x |  | = | 0
| Drinking Fountain - Public | 2 | x |  | = | 0
| Kitchen Sink | 2.2 | x |  | = | 0
| Lavatory | 1.5 | x |  | = | 0 | [5 empty] | Meter Drop Down
| Showerhead (Shower Only) | 2.5 | x |  | = | 0 | [5 empty] | 25 GPM - 5/8” Ultrasonic
| Service Sink | 4 | x |  | = | 0 | [5 empty] | 55 GPM - 1” Ultrasonic
| Toilet – Flush Valve | 35 | x |  | = | 0 | [5 empty] | 500 GPM - 3" Ultrasonic
| - Tank Type | 4 | x |  | = | 0 | [5 empty] | 1250 GPM - 4” Ultrasonic
| Urinal – Pedestal Flush Valve | 35 | x |  | = | 0 | [5 empty] | 2000 GPM - 6” Ultrasonic
| - Wall Flush Valve | 16 | x |  | = | 0
| Wash Sink (Each Set of Faucets) | 4 | x |  | = | 0
| Dishwasher | 2 | x |  | = | 0
| Washing Machine | 6 | x |  | = | 0
| Hose (50 ft Wash Down) - 1/2 in. | 5 | x |  | = | 0
| - 5/8 in. | 9 | x |  | = | 0
| - 3/4 in. | 12 | x |  | = | 0 | [6 empty] | Table 4-1 - Pressure Adj.Factor dropdown
35 PSI - 0.74
| Combined Fixture Value Total |  |  |  | = | 0 | [6 empty] | 40 PSI - 0.80
50 PSI - 0.90
|  | Pressure Adjustment Factor: | [5 empty] | Select Pressure Adjustment Factor from Dropdown box |  |  |  |  | 60 PSI - 1.00
|  | Water Flow Demand: | 0 GPM | [9 empty] | 70 PSI - 1.09
|  |  | . | [9 empty] | 80 PSI - 1.17
| Customer Peak Demand |  | (Press.Adj.Factor ) X (Water Flow Demand) = |  |  |  |  | 0 | GPM |  |  |  | 90 PSI - 1.25
Add Irrigation
Irrigation areas must be divided into zones, with a maximum irrigation demand of 25 GPM.Provide a detailed irrigation plan and calculations with appropriately designed zones.
[6 empty] | GPM |  | 0 | GPM
| Added Fixed Load | [9 empty] | 5/8” | 25 |  | 25 GPM - 5/8” Ultrasonic
| Provide detailed description and backup for this demand. |  |  |  |  | GPM |  | 0 | GPM |  | 1” | 55 |  | 55 GPM - 1” Ultrasonic
[11 empty] | 3" | 500 |  | 500 GPM - 3" Ultrasonic
[7 empty] | TOTAL FIXED DEMAND | 0 | GPM |  | 4” | 1250 |  | 1250 GPM - 4” Ultrasonic
[11 empty] | 6” | 2000 |  | 2000 GPM - 6” Ultrasonic
|  |  |  | Select Meter Size/type: |  |  |  |  | Select Meter from Dropdown box
Figure 4-5 Water customer data sheet Adapted from AWWA Manual M22
| Neptune Water Meter Operating Characteristics |  |  |  |  | Neptune Water Meter Components
| Meter Type | Max. Operating (gpm)
Positive Displacement
| 5/8" | 20
| 3/4" | 30
| 1" | 50
| 1 1/2" | 100
| 2" | 160
Ultrasonic
| 5/8” | 25
| 1” | 55
| 3" | 500
| 4” | 1250
| 6” | 2000